## Slide 1: Stability of coupled synchronous generators

## Slide 2: A warning about the use of reduced models of synchronous generators
Elad Venezian and George Weiss
School of EE, Tel Aviv University

## Slide 3: Introduction
Approximately 150 years of electricity grid.
The electricity grid is more and more dependent on inverters.
The main power source of the electricity gird is the Synchronous Generator (SG).
The stability concept (in particular, frequency and voltage).
We discuss a single generator connected to an infinite bus. The question is its stability and the region of attraction of the stable equilibrium point.
Reduced model called improved swing equation has been proposed by Zhou and Ohsawa (2009) Monshizadeh et al (2016). We investigate its usefulness for stability analysis.

## Slide 4: SG modeling

## Slide 5: SG modeling
In steady state, we expect to have sinusoidal voltages and currents.
To simplify the stability analysis, we use the Park transformation of the voltages and currents, that maps sinusoidal signals into a fixed point in the state space.
=

## Slide 6: SG modeling
Assuming constant , we can obtain the model
This model is independent of (which is the integral of ).
Prime mover torque is where is constant, and the feedback term is used in order to control the frequency of the grid.

## Slide 7: The improved swing equation model
According to (Monshizadeh et al (2016), Zhou and Ohsawa (2009):
The mechanical dynamics of SG is:
This equation is similar to the third line of the previous model when .
Rewriting the torques as the ratio between the power and the angular velocity:
and
SG dynamics can be rewritten as:

## Slide 8: The classical swing equation model
In order to have more simple model, approximate:
and
SG dynamics can be rewritten as:
This model is known as the classical model (Monshizadeh et al (2016), Machowski at el (2009), Sauer and Pai (1998))

## Slide 9: Single SG connected to an infinite bus:
Infinite bus is modeled as a three state phase AC voltage source.
=
-V where -.
We refer this fourth order nonlinear dynamical system as the fourth order model (FOM).

## Slide 10: Single SG connected to an infinite bus: (ISE)
Using phasor analysis of the electrical power that transformed from the SG to the infinite bus:
Substitute it in the in the general swing equation yields:
We refer this second order nonlinear dynamical system as the Improved Swing Equation (ISE).
The classical model becomes:

## Slide 11: Model reduction
In order to show the relation between the ISE model and the FOM model, we derive the ISE model from the FOM model by applying ideas from singular perturbation analysis.
The FOM structure:
It can be rewritten as:
where
, , .
We regard x as the slow variables, and y as the fast variables.
We solve (temporary equilibrium points of the fast dynamics), which yields

## Slide 12: Model reduction
In order to show the relation between the ISE model and the FOM model, we derive the ISE model from the FOM model by applying ideas from singular perturbation analysis.
The FOM structure:
It can be rewritten as:
where
, , .
We regard x as the slow variables, and y as the fast variables.
We solve (temporary equilibrium points of the fast dynamics), which yields

## Slide 13: Model reduction
Substitute it into to obtain
The model becomes:
This model is called the improved swing equation (ISE), (Monshizadeh et al (2016), Zhou and Ohsawa (2009).

## Slide 14: Simulations
5 KW SG connected to infinite bus
variables with a hat correspond to the reduced model.

## Slide 15: Simulations
1 MW SG

## Slide 16: Simulations
The FOM is locally stable, (eigenvalues of the Jacobian around the equilibrium point are −11.41±376.9i, −508±837i).
The ISE doesn’t have any equilibrium ().

## Slide 17: Simulations
Different region of attraction
- Initial condition of this simulation is within the region of attraction of the reduced model, but outside the region of attraction of the FOM

## Slide 18: Two Identical Coupled SGs (TICSG).

## Slide 19
TICSG Modeling:
Two identical SGs connected in parallel through inductive lines, to a resistive load.
Each SG variables depend on different .

## Slide 20
TICSG Modeling:
,
+

## Slide 21
TICSG Modeling:
Proposition 1:The TICSG system is forward complete, i.e. for any initial state , the (unique) solution of the TICSG system is defined for all .
The proof use the boundedness of the energy of the system:
Proposition 2: We work with the function from above. For all sufficiently large, the set
is invariant under the flow of the TICSG system.

## Slide 22
Sketch of the proof:

## Slide 23
TICSG Modeling:
Consider the angle modulo , so that the seventh coordinate of the state is no longer in but instead in the unit circle .
New state space , with the natural mapping from to .
is a compact invariant set for the TICSG system in the state space .

## Slide 24
The equilibrium points of the TICSG model:
The synchronization subspace
The anti-synchronization subspace
The synchronization manifold
=
The anti-synchronization manifold
’ =

## Slide 25
The equilibrium points of the TICSG model:
Proposition 3: Any equilibrium point for the TICSG system in is either in or in ’ .
Proposition 4: The TICSG system has at least one equilibrium point on synchronization subspace .

## Slide 26
The stability of the TICSG system:
The TICSG system:
It can be rewritten as:

## Slide 27
The stability of the TICSG system:

## Slide 28
The stability of the TICSG system:
The synchronization subspace becomes .
, which shows that is invariant.

## Slide 29
The stability of the TICSG system:
Proposition 5: The system with state space , is globally exponentially stable if .
The proof use the Lyapunov function:
where
- It shows that the TICSG system has exactly one equilibrium point in .

## Slide 30
The stability of the TICSG system:
,
- invariant compact subset of .

## Slide 31
Properties of systems: (introduced by V. Andrieu, B. Jayawardhana and L. Praly)
TULES-NL (transversal uniform local exponential stability on ) There exist positive numbers , and such that for all with and , the solution satisfies .
UES-TL (uniform exponential stability for the transversally linear system on ) There exist positive real numbers and such that any solution , of the transversally linear system , satisfies, for all , and , .

## Slide 32
Theorem 1: Suppose that the system satisfies the following conditions:
1. There exist a positive real number , such that:
, .
2. There exists a matrix , such that the function : given by exists, where is The state transition matrix ().
3. There exist positive numbers and such that, for all with ,
,
, 
Then the UES-TL property implies the TULES-NL property for this system.

## Slide 33
Proposition 6: Suppose that system is such that is globally exponentially stable on , with the equilibrium point . Moreover, we assume that the matrix is stable (Hurwitz). Then for every compact set contained in the interior of there exists such that the set
is contained in the region of attraction of the equilibrium point of the system.

## Slide 35
Theorem 2: Assume that the TICSG system satisfies , is a stable (Hurwitz) matrix, and moreover, there exist positive numbers and such that for all with ,
There exist strictly positive real numbers , and such that for all where and the solution satisfies . Namely the manifold is exponentially stable locally in , uniformly in .

## Slide 37: Simulations for TICSG system with 5KW SGs

## Slide 38: Simulations a system that satisfies the conditions of Theorem 2, with initial state inside/outside the region of attraction of the equilibrium point.

## Slide 39: Simulations for TICSG system with 5KW SGs

## Slide 40: A simulation example with unstable E manifold