## Slide 1
Coping with large electrical disturbances in Israel and throughout the World
Reasons & Challenges
Yasha (Yakov) Hain
Senior Executive VP IEC
Israel Electric Corporation
Generation and Transmission
February 4, 2014

## Slide 2
Large Power Disturbances Survey (2000-2012)
Reasons and challenges for disturbances
Challenges of renewable energy penetration
Samples of Israeli System disturbances
Israeli system risk management
Summary & Questions
The presentation subjects

## Slide 3
Historical Power Outages
Aug. 14, 2003
The worst US blackout.
Power line problems in the Midwest trigger a cascade of breakdowns that cut power to 55 million people in eight states and Canada, some for more than day
55 Mil
Sep. 28, 2003
A short circuit in power line in Switzerland leads to blackouts affecting 95% of Italy. Some 55 million people are without power for as long as 18 hours.
55 Mil
July 12, 2004
Heavy use of air conditioners and other factors are blamed for blackouts affecting at least 7 million people in Greece just a month before the Summer Olympic Games.
Aug. 18, 2005
An imbalanced power grid kicks power plants offline in Indonesia leaves almost 100 million people in the dark, many for more than five hours.
100 Mil
10 Mil
7 Mil
November, 2006
A German power company switches off high voltage line over a river to let a cruise ship pass. It triggers outages for 10 million people in Germany, France, Italy and Spain.
370 Mil
Sep. 8, 2011
System disturbance occurred leaded to cascading outages and leaving approximately 5 million people without power. The outages affected parts of Arizona, California, Mexico.
60 Mil
Nov.10, 2009
Storms near the Itaipu hydroelectric dam on the Paraguay-Brazil border blamed for outages that cut power to as many as 60 million people in Brazil for couple hours. The Paraguay population of 7 million is also blacked out.
5 Mil
July.30, 2012
India’s northern electricity grid fails for much of the day, leaving 370 million people without power.
620 Mil
July 31, 2012
3 power grids across half of India fail in what authorities call overdrawing of the system, leaving a record 620 million people without power for raising concerns about ability to supply
demands.
Source: news.Nationalpost.com
Since 2000

## Slide 4
US & Canada Blackout - facts
Source: US & Canada Power system Outage task force- Causes of August 14 blackout
The largest blackout in north America ever:
45 million in USA, 10 million in Canada were affected
62 000 MW of power outages
508 generating units in 256 power plants shut down
    Conventional -66
    Combustion including Combine cycle -70
    Nuclear -10
    Hydro -101 and other -18
Estimated total cost in USA 10.3 billion $,
Canada 2.3 billion $
Time of restoration 50%- 24 hours, 80%-48 hours
the rest up to 5 days

## Slide 5
Large Power Disturbances Survey (2000-2012)
Reasons and challenges for disturbances
Challenges of renewable energy penetration
Samples of Israeli System disturbances
Israeli system risk management
Summary & Questions
Main presentation subjects

## Slide 6
Swiss cheese fault model
Operators inter communication fault
Cascade lines and generations tripping
SYSTEM
COLLAPSE
345 KV line fault due tree touch, some power plant fault
State estimator confused by line fault and Alarm system fault
Inadequate tree trimming
US & Canada largest blackout on August 14, 2003
Notes: מודל גבינה שוויצרית הינו מודל אשר אומר באם בגבינה ישנם חורים ולקחת ולחתוך את הגבינה לחתיכות סיכוי קלוש שכל החורים במקומות שונים בפרוסות יסתדרו בקו אחד.
זאת אומרת צריך השתלשלות אירועים ונסיבות אשר עלולה לגרום לאירוע כלשהו
בדומה לכך נעשה ניתוח של האירוע בצפון אמריקה.

## Slide 7
Failure to maintain adequate reactive power support
Failure to ensure operation within secure limits
Inadequate vegetation management
Inadequate Operators training
Failure to identify emergency conditions and
communication with neighboring systems
Inadequate regional-scale visibility over the
power system, dysfunction of EMS/SCADA system
Lack of adequate backup capability of the EMS system
Direct causes for US blackout
Source: US & Canada Power system Outage task force- Causes of August 14 blackout
Notes: REACTIVE POWER – לא הייתה בארה"ב דרישה מNERC ליצור הספק ראקטיבי – כי פשוט לא שילמו עבורו. ולכן בסופו של דבר התרחש VOLTAGE COLLAPSE
SECURE LIMITS – המערכת נוהלה ברמות נמוכות מה תקין של מתחים בשל הפסקות מעגלים לעבודות שונות וכי לא נעשה תכנון נכון
VEGETATION MANAGEMENT – מדיניות גיזום עצים לא עבדה טוב ולכן אל כל הגיזום נעשה לקראת שיא קיץ
OPERATORS TRAINING – לא היה מספיק כלל אימון של מפקחים למצבים שונים כולל סימולאטור המדמה את המערכת בשלמותה
EMERGENCY COMMUNICATION - - בשל כשל במערכת STATE ESTIMATOR פיקוח MISO הגוף המפקח על פיקוחים איזורים רבים לא היה מסוגל לזהות תמונה בפועל
כמו כו שאננות של מפקחים בפיקוח FE שמערכת התראות שלו כשלה גרם לחוסר אימון במידע אשר נמסר מפיקוחים סמוכים
POWER SYSTEM VISIBILITY - בשל חוסר במדידות של חלק ממידע אשר קיים בפיקוחים איזורים לא ניתן היה לראות את התמונה המלאה. בנוסף מערכת SCADA נפלה ולא היתה מערכת גיבוי נוספת אשר אמורה להתריע על מצב סיכון , כמו כן תוכנות לחישוב של מצב המערכת וכלל חוסר פיקודים במערכת בעת האירוע בפיקוח FE

## Slide 8
Main reasons for large disturbances
Source: Cigre, WG 2.21 report, 2012
Total contribution | Secondary | Primary | Root cause | #
3 | 0 | 3 | Primary equipment failure | 1
5 | 1 | 4 | Design and application errors | 2
2 | 1 | 1 | Secondary equipment failure | 3
5 | 1 | 4 | Communication failure | 4
6 | 0 | 6 | Natural phenomena | 5
5 | 0 | 5 | Operator errors | 6
1 | 0 | 1 | Errors in maintenance | 7
0 | 0 | 0 | Security related (sabotage, etc.) | 8
1 | 0 | 1 | Inadequate investment and complexity of system | 9
Based on 16 large disturbances in the World 2002 - 2011

## Slide 9
A part from natural phenomena
the main causes for most events are:
  Operators errors
  Communication failure (including lack of situation awareness)
  Protection relay mis- coordination (design) or operations
Control Center Performance
  Nothing suggests that any system control centers
  exhibited below expectation performance
To be improved
  Situation awareness
  Protection system design coordination and verification
  Operator training and adherence to established procedures
Lessons Learnt
Source: Cigre, WG 2.21 report, 2012

## Slide 10
Large Power Disturbances Survey (2000-2012)
Reasons and challenges for disturbances
Challenges of renewable energy penetration
Samples of Israeli System disturbances
Israeli system risk management
Summary & Questions
Main presentation subjects

## Slide 11
United Europe Grid
Source: Cigre, WG 2.21 report, 2012

## Slide 12
In Germany approx. 12.7GW of DG – mostly photovoltaic (PV)
Technical guideline since 2005 applied to DG – Distributed
Generation in low voltage grids :
  Disconnection within 200 ms, if f<=47.5 Hz or f>=50.2 Hz
  Reconnection after 30 s, if 47.5 Hz< f <50.2 Hz
  50.2 Hz was chosen for an easy operation of standby
  power by DSO
With several GW of DG in the interconnected system
frequency stability is hampered if 50.2 Hz are exceeded
Frequency stability:
  Acceleration time constant is approx. 10s (in future
  probably decreasing due to power electronics.
  Primary control reserve is 3000 MW
Introduction 50.2 Hz problem
Source: Cigre, WG 2.21 report, 2012

## Slide 13
Triggering 50.2 Hz problem
Low probability to exceed 50.2 Hz under normal conditions
- Frequency measurements during European disturbance 2006 - 50.2 Hz are significantly exceeded
Source: Cigre, WG 2.21 report, 2012

## Slide 14
New Grid connections rules
Source: Cigre, WG 2.21 report, 2012

## Slide 15
50.2 HZ - Conclusions
DG-infeed has reached a system relevant penetration
and is furthermore growing
An integral approach over all voltage levels of the united
grid is needed
In Germany the “System stability regulation” started
since July 2012 for PV retrofit in:
    Cost of 175 million euro
    Approx. 9500 MW of installed LV PV
    Timeframe – 3 years
Development of grid codes e.g. “Requirements for Grid
Connection Applicable to all Generators”
Studies of system Dynamics with respect to DG
in Continental Europe is needed
Source: Cigre, WG 2.21 report, 2012

## Slide 16
Large Power Disturbances Survey (2000-2012)
Reasons and challenges for disturbances
Challenges of renewable energy penetration
Samples of Israeli System disturbances
Israeli system risk management
Summary & Questions
Main presentation subjects

## Slide 17
Bar
21:20
Noble
Shut down
08:45
End of
event
22:40
Noble
Is back
Noble disturbance 31/7/2011

## Slide 18
Bar
4924
2640
2135
4908
1577
2104
563
4861
1305
547
1170
- Coal
- Gas
- Gas oil
- Fuel Oil
Chain of events
4% during 1 HOUR
Lowest
reserve

## Slide 19
Bar
4924
2640
2135
4908
1577
2104
563
4861
1305
547
1170
21:28
אשכול 3
צפית 2
21:32
21:28
21:28
21:28
21:28
- Unit Start
- Load reduction
21:25
רידינג 4
אשכול 10
21:43
רמת חובב 4
+ דוד
22:12
חגית 5
+ דוד
22:17
22:27
גזר 30
חגית 20
22:40
אשכול 9+6
22:08
22:39
אשכול 8
22:39
אשכול 7
חגית 4 + דוד
23:47
Chain of events
- Fuel transfer completion
- Shut down

## Slide 20
System capacity
9850 MW
7.5 hours
5 hours
5.5 hours
Transmission constraints
9750 MW
Transmission constraints in case of N-1
9550 MW
What might happened?
Explanation
Outages because of generation lack during 3 days up to 250MW
Additional outages because of line overload in Tel Aviv area – 100MW
Additional outages in case of N-1 fault in South to Hadera – 200MW
550
550
550
Power outages

## Slide 21
Hagit PRMS Shutdown
20.09.2010
Hagit site
shutdown
Hagit came
back
MW
90 MINUTES
POWER OUTAGES
Power
Outages
Load Shedding 1
Power
Outages
Load
Shedding 2
Customers
Lost
Hz
Customer damage –
Unsupplied Energy 256 MWh
Alternative fuel cost 0.8 mil$
Up to 1.5 hour customer shortage
Notes: חשוב לציין כאן שהאירוע לא נגרם עקב תקלה בחח"י אלא עקב טעות אנוש בחברת נתג"ז באחריותה מתקני PRMS
באירוע נפסק אתר חגית בהספק של כ960 MW
האירוע התרחש בפסגת עומס בשעה 14

## Slide 22
Large Power Disturbances Survey (2000-2012)
Reasons and challenges for disturbances
Challenges of renewable energy penetration
Samples of Israeli System disturbances
Israeli system risk management
Summary & Questions
Main presentation subjects

## Slide 23
  Isolated system
  Low system reserve
  Not enough IPPs coming yet
  Generation by fuel - Natural Gas Dependency
  A lot of environmental constraints
  Large future renewable PV penetration
  A lot of players IEC, IPPs, PUA, Gas Authority
  and others
Israeli Grid Constraints

## Slide 24
System risk and response
Maintenance activities coordination
Supplier disturbances:
    Gas quality
    Facilities fault
Transporter - INGL :
    No pressure regulation ability
    One PRMS to Power Plants
    Radial pipeline – no redundancy
Disturbance management – a lot of players
IEC alternative fuel generation response
Low grid reserve (5%) – virtual gas storage

## Slide 25
Large Power Disturbances Survey (2000-2012)
Reasons and challenges for disturbances
Challenges of renewable energy penetration
Samples of Israeli System disturbances
Israeli system risk management
Summary & Questions
Main presentation subjects

## Slide 26
Summary
Power outages happen and utilities
have to be prepared to deal with them
The mean time between large outages
more than 10000 MW is 13 years*
The largest power outage in Israel
happened in 1995 ………………
*California Institute of Technology, “Complexity and Robustness,” 1999. Data from NERC

## Slide 27
And finally

## Slide 28
Questions
Thanks
and
your